## Residenziale
| Weekday | [10 empty] | Weekend
Carico | Occupancy (Sensible) | Appliances | Lighting | Vapour FlowRate | Infiltration FlowRate | Plant Availability | Ventilation FlowRate | HeatSP | CoolSP | HumSP | DehumSP | Occupancy (Sensible) | Appliances | Lighting | Vapour FlowRate | Infiltration FlowRate | Plant Availability | Ventilation FlowRate | HeatSP | CoolSP | HumSP | DehumSP
Unità di misura | [W/m²] | [W/m²] | [W/m²] | [g/(m² s)] | [Vol/h] | [-] | [m³/(s m²)] | [°C] | [°C] | [%] | [%] | [W/m²] | [W/m²] | [W/m²] | [g/(m² s)] | [Vol/h] | [-] | [m³/(s m²)] | [°C] | [°C] | [%] | [%]
Valore nominale | 2.8 | 3 | 3 | 0.00058889 | 0.2 | 1 | 0.0005 | 1 | 1 | 1 | 1 | 2.8 | 3 | 3 | 0.00058889 | 0.2 | 1 | 0.0005 | 1 | 1 | 1 | 1
1:00 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
2:00 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
3:00 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
4:00 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
5:00 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
6:00 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
7:00 | 0.5 | 0.5 | 0.15 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.5 | 0.15 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
8:00 | 0.5 | 0.7 | 0.15 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.7 | 0.15 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
9:00 | 0.5 | 0.7 | 0.15 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.7 | 0.15 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
10:00 | 0.1 | 0.5 | 0.15 | 0.1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.5 | 0.15 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
11:00 | 0.1 | 0.5 | 0.05 | 0.1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.5 | 0.05 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
12:00 | 0.1 | 0.6 | 0.05 | 0.1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.6 | 0.05 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
13:00 | 0.1 | 0.6 | 0.05 | 0.1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.6 | 0.05 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
14:00 | 0.2 | 0.6 | 0.05 | 0.2 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.6 | 0.05 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
15:00 | 0.2 | 0.6 | 0.05 | 0.2 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.6 | 0.05 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
16:00 | 0.2 | 0.5 | 0.05 | 0.2 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.5 | 0.05 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
17:00 | 0.5 | 0.5 | 0.2 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.5 | 0.2 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
18:00 | 0.5 | 0.7 | 0.2 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.7 | 0.2 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
19:00 | 0.5 | 0.7 | 0.2 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.7 | 0.2 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
20:00 | 0.8 | 0.8 | 0.2 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.8 | 0.2 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
21:00 | 0.8 | 0.8 | 0.2 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.8 | 0.2 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
22:00 | 0.8 | 0.8 | 0.2 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.8 | 0.8 | 0.2 | 0.8 | 1 | 1 | 1 | 20 | 26 | 0 | 60
23:00 | 1 | 0.6 | 0.15 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 0.6 | 0.15 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
24:00 | 1 | 0.6 | 0.15 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 0.6 | 0.15 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60

## Terziario
| Weekday | [10 empty] | Weekend
Carico | Occupancy (Sensible) | Appliances | Lighting | Vapour FlowRate | Infiltration FlowRate | Plant Availability | Ventilation FlowRate | HeatSP | CoolSP | HumSP | DehumSP | Occupancy (Sensible) | Appliances | Lighting | Vapour FlowRate | Infiltration FlowRate | Plant Availability | Ventilation FlowRate | HeatSP | CoolSP | HumSP | DehumSP
Unità di misura | [W/m²] | [W/m²] | [W/m²] | [g/(m² s)] | [Vol/h] | [-] | [m³/(s m²)] | [°C] | [°C] | [%] | [%] | [W/m²] | [W/m²] | [W/m²] | [g/(m² s)] | [Vol/h] | [-] | [m³/(s m²)] | [°C] | [°C] | [%] | [%]
Valore nominale | 4.7 | 12 | 12 | 0.00098056 | 0.2 | 1 | 0.0008 | 1 | 1 | 1 | 1 | 4.7 | 12 | 12 | 0.00098056 | 0.2 | 1 | 0.0008 | 1 | 1 | 1 | 1
1:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
2:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
3:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
4:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
5:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
6:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
7:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
8:00 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
9:00 | 0.6 | 0.6 | 0.6 | 0.6 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
10:00 | 0.6 | 0.6 | 0.6 | 0.6 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
11:00 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
12:00 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
13:00 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
14:00 | 0.6 | 0.6 | 0.6 | 0.6 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
15:00 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
16:00 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
17:00 | 0.6 | 0.6 | 0.6 | 0.6 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
18:00 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
19:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
20:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
21:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
22:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
23:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
24:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100

## Servizi
| Weekday | [10 empty] | Weekend
Carico | Occupancy (Sensible) | Appliances | Lighting | Vapour FlowRate | Infiltration FlowRate | Plant Availability | Ventilation FlowRate | HeatSP | CoolSP | HumSP | DehumSP | Occupancy (Sensible) | Appliances | Lighting | Vapour FlowRate | Infiltration FlowRate | Plant Availability | Ventilation FlowRate | HeatSP | CoolSP | HumSP | DehumSP
Unità di misura | [W/m²] | [W/m²] | [W/m²] | [g/(m² s)] | [Vol/h] | [-] | [m³/(s m²)] | [°C] | [°C] | [%] | [%] | [W/m²] | [W/m²] | [W/m²] | [g/(m² s)] | [Vol/h] | [-] | [m³/(s m²)] | [°C] | [°C] | [%] | [%]
Valore nominale | 13.8 | 0 | 8 | 0.0030861 | 0.25 | 1 | 0 | 1 | 1 | 1 | 1 | 13.8 | 8 | 8 | 0.0030861 | 0.15 | 1 | 0.0038 | 1 | 1 | 1 | 1
1:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
2:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
3:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
4:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
5:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
6:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
7:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
8:00 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
9:00 | 0.6 | 0.6 | 0.6 | 0.6 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
10:00 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
11:00 | 0.6 | 0.6 | 0.6 | 0.6 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
12:00 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
13:00 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
14:00 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
15:00 | 0.6 | 0.6 | 0.6 | 0.6 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
16:00 | 0.4 | 0.4 | 0.4 | 0.4 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
17:00 | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
18:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
19:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
20:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
21:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
22:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
23:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
24:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100

## Commerciale
| Weekday | [10 empty] | Weekend
Carico | Occupancy (Sensible) | Appliances | Lighting | Vapour FlowRate | Infiltration FlowRate | Plant Availability | Ventilation FlowRate | HeatSP | CoolSP | HumSP | DehumSP | Occupancy (Sensible) | Appliances | Lighting | Vapour FlowRate | Infiltration FlowRate | Plant Availability | Ventilation FlowRate | HeatSP | CoolSP | HumSP | DehumSP
Unità di misura | [W/m²] | [W/m²] | [W/m²] | [g/(m² s)] | [Vol/h] | [-] | [m³/(s m²)] | [°C] | [°C] | [%] | [%] | [W/m²] | [W/m²] | [W/m²] | [g/(m² s)] | [Vol/h] | [-] | [m³/(s m²)] | [°C] | [°C] | [%] | [%]
Valore nominale | 13.09 | 40 | 30 | 0.004284 | 0.2 | 1 | 0.0020833 | 1 | 1 | 1 | 1 | 13.09 | 40 | 30 | 0.004284 | 0.2 | 1 | 0.0020833 | 1 | 1 | 1 | 1
1:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
2:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
3:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
4:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
5:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
6:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
7:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
8:00 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 20 | 26 | 0 | 60
9:00 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 20 | 26 | 0 | 60
10:00 | 0 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 20 | 26 | 0 | 60
11:00 | 0.2 | 1 | 1 | 0.2 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.1 | 1 | 1 | 0.1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
12:00 | 0.2 | 1 | 1 | 0.2 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60
13:00 | 0.3 | 1 | 1 | 0.3 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60
14:00 | 0.3 | 1 | 1 | 0.3 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60
15:00 | 0.3 | 1 | 1 | 0.3 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
16:00 | 0.3 | 1 | 1 | 0.3 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
17:00 | 0.3 | 1 | 1 | 0.3 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
18:00 | 0.3 | 1 | 1 | 0.3 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
19:00 | 0.1 | 1 | 1 | 0.1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.5 | 1 | 1 | 0.5 | 1 | 1 | 1 | 20 | 26 | 0 | 60
20:00 | 0.1 | 1 | 1 | 0.1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.3 | 1 | 1 | 0.3 | 1 | 1 | 1 | 20 | 26 | 0 | 60
21:00 | 0.1 | 1 | 1 | 0.1 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0.1 | 1 | 1 | 0.1 | 1 | 1 | 1 | 20 | 26 | 0 | 60
22:00 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 20 | 26 | 0 | 60 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 20 | 26 | 0 | 60
23:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100
24:00 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 16 | 32 | 0 | 100